## Summary
FROM: | Mark Biegert
SUBJECT: | Distribution Summary
DATE: | 2016-11-30
Key Assumptions
| Temperature level assumes bundling limits |  | Reference
| Cat 5e current limit of 600 mA per pair |  | Reference
| Allowed 15 °C temperature rise |  | Reference
| Most cables have max temp of 60°C |  | Reference
| Maximum wire temperature of 75 °C |  | Reference
| Measure data on temperature rise is available |  | Reference
Length Data
Reference Material
MC Communications Paper
Panduit Whitepaper
Leviton Blog

## ReachFormula
FROM: | Mark Biegert
SUBJECT: | Wire Reach Table
DATE: | 2016-11-27
Model
Schematic
Equations
Where
n is the wire gauge (AWG)
d is the wire diameter (mm)
IL is the load current (A)
VS is the source voltage (V)
VL is the load voltage (V)
T is the temperature (°C)
kCu is copper's temperature coefficient of resistance (Ω-m)
RC is the contact resistance (Ω)
L is the cable length (m)
λCu is the resistance of a unit length of copper wire (Ω/m)
P is the load power (W)
LMax is the maximum length or reach (m)
All calculations are done in metric, final conversion is to feet.
Parameters
| Description | Symbol | Value | Unit | Comment
| Cu Resistivity | _ρCu | 1.7241e-08 | Ω-m | Copper resistivity at 20 °C
| Contact Resistance | _RC | 0.1 | Ω | Commonly used value
| Wire Temperature | _T | 75 | °C | Common PoE Assumption
| Cu Res. Temp Coeff. | _kCu | 0.00393 | /°C | Commonly used value
| Source Voltage | _vS | 57 | V | Problem statement
Reach Table
[8 empty] | Load Current (A) |  | Reach (ft)
| AWG | Wire Pairs | Load Power (W) | Wire Diameter (mm) | Wire Area (mm2) | 1 m Cable Resistance (Ω) @ 20 °C | 1 m Cable Resistance (Ω) @ 75 °C | 44 | 50 | 44 | 50
| 25 | 4 | 40 | 0.04547% | 1.624e-05% | 0.10619 | 0.12914 | 0.90909 | 0.8 | 706.2449 | 424.255
| 25 | 4 | 70 | 0.04547% | 1.624e-05% | 0.10619 | 0.12914 | 1.5909 | 1.4 | 394.8584 | 233.7213
| 25 | 4 | 90 | 0.04547% | 1.624e-05% | 0.10619 | 0.12914 | 2.0455 | 1.8 | 302.5957 | 177.2669
| 24 | 4 | 40 | 0.05106% | 2.047e-05% | 0.084213 | 0.10242 | 0.90909 | 0.8 | 890.5583 | 534.9757
| 24 | 4 | 70 | 0.05106% | 2.047e-05% | 0.084213 | 0.10242 | 1.5909 | 1.4 | 497.9072 | 294.7172
| 24 | 4 | 90 | 0.05106% | 2.047e-05% | 0.084213 | 0.10242 | 2.0455 | 1.8 | 381.5662 | 223.5294
| 23 | 4 | 40 | 0.05733% | 2.582e-05% | 0.066784 | 0.08122 | 0.90909 | 0.8 | 1122.9733 | 674.5919
| 23 | 4 | 70 | 0.05733% | 2.582e-05% | 0.066784 | 0.08122 | 1.5909 | 1.4 | 627.8494 | 371.6315
| 23 | 4 | 90 | 0.05733% | 2.582e-05% | 0.066784 | 0.08122 | 2.0455 | 1.8 | 481.1461 | 281.8654
| 18 | 1 | 40 | 0.1024% | 8.23e-05% | 0.020948 | 0.025476 | 0.90909 | 0.8 | 895.0448 | 537.6708
| 18 | 1 | 70 | 0.1024% | 8.23e-05% | 0.020948 | 0.025476 | 1.5909 | 1.4 | 500.4156 | 296.2019
| 18 | 1 | 90 | 0.1024% | 8.23e-05% | 0.020948 | 0.025476 | 2.0455 | 1.8 | 383.4884 | 224.6555
| 20 | 1 | 40 | 0.08118% | 5.176e-05% | 0.033308 | 0.040508 | 0.90909 | 0.8 | 562.8992 | 338.1445
| 20 | 1 | 70 | 0.08118% | 5.176e-05% | 0.033308 | 0.040508 | 1.5909 | 1.4 | 314.7145 | 186.2832
| 20 | 1 | 90 | 0.08118% | 5.176e-05% | 0.033308 | 0.040508 | 2.0455 | 1.8 | 241.1782 | 141.2873
Reduced Form Based on Formulas Filled Down | [7 empty] | Camera Image of Same Data Using Table Method
Reach (ft)
| Wire Type | AWG | Wire Pairs | Load Power (W) | 44 | 50
| Cat5 | 25 | 4 | 40 | 706.2449 | 424.255
| Cat5 | 25 | 4 | 70 | 394.8584 | 233.7213
| Cat5 | 25 | 4 | 90 | 302.5957 | 177.2669
| Cat5e | 24 | 4 | 40 | 890.5583 | 534.9757
| Cat5e | 24 | 4 | 70 | 497.9072 | 294.7172
| Cat5e | 24 | 4 | 90 | 381.5662 | 223.5294
| Cat6 | 23 | 4 | 40 | 1122.9733 | 674.5919
| Cat6 | 23 | 4 | 70 | 627.8494 | 371.6315
| Cat6 | 23 | 4 | 90 | 481.1461 | 281.8654
| Copper Pair | 18 | 1 | 40 | 895.0448 | 537.6708
| Copper Pair | 18 | 1 | 70 | 500.4156 | 296.2019
| Copper Pair | 18 | 1 | 90 | 383.4884 | 224.6555
| Copper Pair | 20 | 1 | 40 | 562.8992 | 338.1445
| Copper Pair | 20 | 1 | 70 | 314.7145 | 186.2832
| Copper Pair | 20 | 1 | 90 | 241.1782 | 141.2873

## ReachTable
FROM: | Mark Biegert
SUBJECT: | Wire Reach Table
DATE: | 2016-11-27
Parameters
| Description | Symbol | Value | Unit | Comment
| Cu Resistivity | _ρCu | 1.7241e-08 | Ω-m | Copper resistivity at 20 °C
| Contact Resistance | _RC | 0.1 | Ω | Commonly used value
| Wire Temperature | _T | 75 | °C | Common PoE Assumption
| Cu Res. Temp Coeff. | _kCu | 0.393% | /°C | Commonly used value
| Source Voltage | _vS | 57 | V | Problem statement
Example Calculation
| Wire Gauge | 20 | AWG
| Pairs | 1
| Load Power | 70 | W
| Load Voltage | 50 | V
| Load Current | 1.4 | A
| Wire Diameter | 0.08118% | mm2
| Wire Area | 5.176e-05% | mm2
| Unit Resistance | 0.040508 | Ω/m
| Reach | 186.2832 | ft | This is the reach
| Row | 1900-01-13 | Points to the row
| Column | 1900-01-01 | Points to the column
Reduced Form
| Row 34 and Column G hidden | [5 empty] | Reach (ft)
|  | Wire Type | AWG | Wire Pairs | Load Power (W) | Index | 44 | 50
[6 empty] | 186.2832 | 1899-12-31 | 1900-01-01 | `
|  | Cat5 | 25 | 4 | 40 | 1899-12-31 | 706.2449 | 424.255
|  | Cat5 | 25 | 4 | 70 | 1900-01-01 | 394.8584 | 233.7213
|  | Cat5 | 25 | 4 | 90 | 1900-01-02 | 302.5957 | 177.2669
|  | Cat5e | 24 | 4 | 40 | 1900-01-03 | 890.5583 | 534.9757
|  | Cat5e | 24 | 4 | 70 | 1900-01-04 | 497.9072 | 294.7172
|  | Cat5e | 24 | 4 | 90 | 1900-01-05 | 381.5662 | 223.5294
|  | Cat6 | 23 | 4 | 40 | 1900-01-06 | 1122.9733 | 674.5919
|  | Cat6 | 23 | 4 | 70 | 1900-01-07 | 627.8494 | 371.6315
|  | Cat6 | 23 | 4 | 90 | 1900-01-08 | 481.1461 | 281.8654
|  | Copper Pair | 18 | 1 | 40 | 1900-01-09 | 895.0448 | 537.6708
|  | Copper Pair | 18 | 1 | 70 | 1900-01-10 | 500.4156 | 296.2019
|  | Copper Pair | 18 | 1 | 90 | 1900-01-11 | 383.4884 | 224.6555
|  | Copper Pair | 20 | 1 | 40 | 1900-01-12 | 562.8992 | 338.1445
|  | Copper Pair | 20 | 1 | 70 | 1900-01-13 | 314.7145 | 186.2832
|  | Copper Pair | 20 | 1 | 90 | 1900-01-14 | 241.1782 | 141.2873
These are parameters that are varying