{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["ConduitBending","FormulaFillDown","BendRadiusVersion"],"not_rendered":{"charts":0,"images":3,"macros":1,"external_links":0,"defined_names":15,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"ConduitBending","index":0,"n_rows":121,"n_cols":24,"rows_kept":121,"cut":false,"hidden":false,"merged":[]}
[null,"FROM:","Mark Biegert"]
[null,"SUBJECT:","Conduit Bending Table"]
[null,"DATE:",{"$f":"TEXT(43110,\"dd-mmm-yyy\")","v":"10-Jan-2018"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"My Shrinkage and Offset Table"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Angle (°)",null,"Shrinkage","Bend Multiple"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"S8","v":6.25E-2},1,2]
[null,"Prototype Calculation (i.e. Work One Example)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"row",1,null,10,1,6.25E-2,5.7587999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"col",1,null,22.5,2,0.1875,2.6131000000000002]
[null,"Parameter","Symbol","Value","Unit",null,null,null,null,null,null,null,null,null,null,null,null,"result",{"$f":"INDEX(D10:D11,S7)","v":6.25E-2},null,30,3,0.25,2]
[null,"Bend Angle","_Θ",45,"deg",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,45,4,0.4375,1.4141999999999999]
[null,"Shrinkage","_S",{"$f":"MROUND((TAN(INDEX(U6:U10,S6)*PI()/360)),1/16)","v":6.25E-2},"in length/inch rise",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,5,0.5625,1.1547000000000001]
[null,"Bend Distance","_BD",{"$f":"ROUND(_xlfn.CSC(INDEX(U6:U10,S6)*PI()/180),4)","v":5.7587999999999999},"in dist./in rise"]
[]
[null,"My Reference Table"]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Published Reference Table"]
[]
[null,"Angle (°)","Shrinkage","Bend Mult."]
[null,10,6.25E-2,5.7587999999999999]
[null,22.5,0.1875,2.6131000000000002]
[null,30,0.25,2]
[null,45,0.375,1.4141999999999999]
[null,60,0.5,1.1547000000000001]
[]
[null,"Calculation Prototypes"]
[]
[null,"Shrinkage",null,null,null,null,null,null,"Bend Offset"]
[]
[null,"Parameter","Value","Unit",null,null,null,null,"Parameter","Value","Unit"]
[null,"Bend Angle",22.5,"deg",null,null,null,null,"Bend Angle",10,"deg"]
[null,"Bend Offset",10,"in",null,null,null,null,"Bend Offset",1,"in"]
[null,"Shrinkage",{"$f":"MROUND(VLOOKUP(C36,_Table,2,0)*C37,1/16)","v":1.875},"in",null,null,null,null,"Bend Dist.",{"$f":"MROUND(VLOOKUP(J36,_Table,3,0)*J37,1/16)","v":5.75},"in"]
[]
[null,"Data Tables"]
[]
[null,"Shrinkage Table",null,null,null,null,null,null,"Bend Distance Table"]
[]
[null,null,"Angle",null,null,null,null,null,null,"Angle"]
[null,{"$f":"C38","v":1.875},10,22.5,30,45,60,null,{"$f":"J38","v":5.75},10,22.5,30,45,60]
[null,0.5,6.25E-2,0.125,0.125,0.1875,0.25,null,0.5,2.875,1.3125,1,0.6875,0.5625]
[null,1,6.25E-2,0.1875,0.25,0.375,0.5,null,1,5.75,2.625,2,1.4375,1.125]
[null,1.5,0.125,0.3125,0.375,0.5625,0.75,null,1.5,8.625,3.9375,3,2.125,1.75]
[null,2,0.125,0.375,0.5,0.75,1,null,2,11.5,5.25,4,2.8125,2.3125]
[null,2.5,0.1875,0.5,0.625,0.9375,1.25,null,2.5,14.375,6.5625,5,3.5625,2.875]
[null,3,0.1875,0.5625,0.75,1.125,1.5,null,3,17.25,7.8125,6,4.25,3.4375]
[null,3.5,0.25,0.6875,0.875,1.3125,1.75,null,3.5,20.125,9.125,7,4.9375,4.0625]
[null,4,0.25,0.75,1,1.5,2,null,4,23.0625,10.4375,8,5.6875,4.625]
[null,4.5,0.3125,0.875,1.125,1.6875,2.25,null,4.5,25.9375,11.75,9,6.375,5.1875]
[null,5,0.3125,0.9375,1.25,1.875,2.5,null,5,28.8125,13.0625,10,7.0625,5.75]
[null,5.5,0.375,1.0625,1.375,2.0625,2.75,null,5.5,31.6875,14.375,11,7.75,6.375]
[null,6,0.375,1.125,1.5,2.25,3,null,6,34.5625,15.6875,12,8.5,6.9375]
[null,6.5,0.4375,1.25,1.625,2.4375,3.25,null,6.5,37.4375,17,13,9.1875,7.5]
[null,7,0.4375,1.3125,1.75,2.625,3.5,null,7,40.3125,18.3125,14,9.875,8.0625]
[null,7.5,0.5,1.4375,1.875,2.8125,3.75,null,7.5,43.1875,19.625,15,10.625,8.6875]
[null,8,0.5,1.5,2,3,4,null,8,46.0625,20.875,16,11.3125,9.25]
[null,8.5,0.5625,1.625,2.125,3.1875,4.25,null,8.5,48.9375,22.1875,17,12,9.8125]
[null,9,0.5625,1.6875,2.25,3.375,4.5,null,9,51.8125,23.5,18,12.75,10.375]
[null,9.5,0.625,1.8125,2.375,3.5625,4.75,null,9.5,54.6875,24.8125,19,13.4375,11]
[null,10,0.625,1.875,2.5,3.75,5,null,10,57.5625,26.125,20,14.125,11.5625]
[null,11,0.6875,2.0625,2.75,4.125,5.5,null,11,63.375,28.75,22,15.5625,12.6875]
[null,12,0.75,2.25,3,4.5,6,null,12,69.125,31.375,24,17,13.875]
[null,13,0.8125,2.4375,3.25,4.875,6.5,null,13,74.875,34,26,18.375,15]
[null,14,0.875,2.625,3.5,5.25,7,null,14,80.625,36.5625,28,19.8125,16.1875]
[null,15,0.9375,2.8125,3.75,5.625,7.5,null,15,86.375,39.1875,30,21.1875,17.3125]
[null,16,1,3,4,6,8,null,16,92.125,41.8125,32,22.625,18.5]
[null,17,1.0625,3.1875,4.25,6.375,8.5,null,17,97.875,44.4375,34,24.0625,19.625]
[null,18,1.125,3.375,4.5,6.75,9,null,18,103.6875,47.0625,36,25.4375,20.8125]
[null,19,1.1875,3.5625,4.75,7.125,9.5,null,19,109.4375,49.625,38,26.875,21.9375]
[null,20,1.25,3.75,5,7.5,10,null,20,115.1875,52.25,40,28.3125,23.125]
[null,21,1.3125,3.9375,5.25,7.875,10.5,null,21,120.9375,54.875,42,29.6875,24.25]
[null,22,1.375,4.125,5.5,8.25,11,null,22,126.6875,57.5,44,31.125,25.375]
[null,23,1.4375,4.3125,5.75,8.625,11.5,null,23,132.4375,60.125,46,32.5,26.5625]
[null,24,1.5,4.5,6,9,12,null,24,138.1875,62.6875,48,33.9375,27.6875]
[null,25,1.5625,4.6875,6.25,9.375,12.5,null,25,144,65.3125,50,35.375,28.875]
[]
[null,"Master Table"]
[]
[null,null,"Angle"]
[null,null,{"$f":"$C$45","v":10},null,{"$f":"$D$45","v":22.5},null,{"$f":"$E$45","v":30},null,{"$f":"$F$45","v":45},null,{"$f":"$G$45","v":60}]
[null,"Bend Offset","Shrinkage","Bend Dist.","Shrinkage","Bend Dist.","Shrinkage","Bend Dist.","Shrinkage","Bend Dist.","Shrinkage","Bend Dist."]
[null,{"$f":"$B$46","v":0.5},{"$f":"$C$46","v":6.25E-2},{"$f":"$J$46","v":2.875},{"$f":"$D$46","v":0.125},{"$f":"$K$46","v":1.3125},{"$f":"$E$46","v":0.125},{"$f":"$L$46","v":1},{"$f":"$F$46","v":0.1875},{"$f":"$M$46","v":0.6875},{"$f":"$G$46","v":0.25},{"$f":"$N$46","v":0.5625}]
[null,{"$f":"$B$47","v":1},{"$f":"$C$47","v":6.25E-2},{"$f":"$J$47","v":5.75},{"$f":"$D$47","v":0.1875},{"$f":"$K$47","v":2.625},{"$f":"$E$47","v":0.25},{"$f":"$L$47","v":2},{"$f":"$F$47","v":0.375},{"$f":"$M$47","v":1.4375},{"$f":"$G$47","v":0.5},{"$f":"$N$47","v":1.125}]
[null,{"$f":"$B$48","v":1.5},{"$f":"$C$48","v":0.125},{"$f":"$J$48","v":8.625},{"$f":"$D$48","v":0.3125},{"$f":"$K$48","v":3.9375},{"$f":"$E$48","v":0.375},{"$f":"$L$48","v":3},{"$f":"$F$48","v":0.5625},{"$f":"$M$48","v":2.125},{"$f":"$G$48","v":0.75},{"$f":"$N$48","v":1.75}]
[null,{"$f":"$B$49","v":2},{"$f":"$C$49","v":0.125},{"$f":"$J$49","v":11.5},{"$f":"$D$49","v":0.375},{"$f":"$K$49","v":5.25},{"$f":"$E$49","v":0.5},{"$f":"$L$49","v":4},{"$f":"$F$49","v":0.75},{"$f":"$M$49","v":2.8125},{"$f":"$G$49","v":1},{"$f":"$N$49","v":2.3125}]
[null,{"$f":"$B$50","v":2.5},{"$f":"$C$50","v":0.1875},{"$f":"$J$50","v":14.375},{"$f":"$D$50","v":0.5},{"$f":"$K$50","v":6.5625},{"$f":"$E$50","v":0.625},{"$f":"$L$50","v":5},{"$f":"$F$50","v":0.9375},{"$f":"$M$50","v":3.5625},{"$f":"$G$50","v":1.25},{"$f":"$N$50","v":2.875}]
[null,{"$f":"$B$51","v":3},{"$f":"$C$51","v":0.1875},{"$f":"$J$51","v":17.25},{"$f":"$D$51","v":0.5625},{"$f":"$K$51","v":7.8125},{"$f":"$E$51","v":0.75},{"$f":"$L$51","v":6},{"$f":"$F$51","v":1.125},{"$f":"$M$51","v":4.25},{"$f":"$G$51","v":1.5},{"$f":"$N$51","v":3.4375}]
[null,{"$f":"$B$52","v":3.5},{"$f":"$C$52","v":0.25},{"$f":"$J$52","v":20.125},{"$f":"$D$52","v":0.6875},{"$f":"$K$52","v":9.125},{"$f":"$E$52","v":0.875},{"$f":"$L$52","v":7},{"$f":"$F$52","v":1.3125},{"$f":"$M$52","v":4.9375},{"$f":"$G$52","v":1.75},{"$f":"$N$52","v":4.0625}]
[null,{"$f":"$B$53","v":4},{"$f":"$C$53","v":0.25},{"$f":"$J$53","v":23.0625},{"$f":"$D$53","v":0.75},{"$f":"$K$53","v":10.4375},{"$f":"$E$53","v":1},{"$f":"$L$53","v":8},{"$f":"$F$53","v":1.5},{"$f":"$M$53","v":5.6875},{"$f":"$G$53","v":2},{"$f":"$N$53","v":4.625}]
[null,{"$f":"$B$54","v":4.5},{"$f":"$C$54","v":0.3125},{"$f":"$J$54","v":25.9375},{"$f":"$D$54","v":0.875},{"$f":"$K$54","v":11.75},{"$f":"$E$54","v":1.125},{"$f":"$L$54","v":9},{"$f":"$F$54","v":1.6875},{"$f":"$M$54","v":6.375},{"$f":"$G$54","v":2.25},{"$f":"$N$54","v":5.1875}]
[null,{"$f":"$B$55","v":5},{"$f":"$C$55","v":0.3125},{"$f":"$J$55","v":28.8125},{"$f":"$D$55","v":0.9375},{"$f":"$K$55","v":13.0625},{"$f":"$E$55","v":1.25},{"$f":"$L$55","v":10},{"$f":"$F$55","v":1.875},{"$f":"$M$55","v":7.0625},{"$f":"$G$55","v":2.5},{"$f":"$N$55","v":5.75}]
[null,{"$f":"$B$56","v":5.5},{"$f":"$C$56","v":0.375},{"$f":"$J$56","v":31.6875},{"$f":"$D$56","v":1.0625},{"$f":"$K$56","v":14.375},{"$f":"$E$56","v":1.375},{"$f":"$L$56","v":11},{"$f":"$F$56","v":2.0625},{"$f":"$M$56","v":7.75},{"$f":"$G$56","v":2.75},{"$f":"$N$56","v":6.375}]
[null,{"$f":"$B$57","v":6},{"$f":"$C$57","v":0.375},{"$f":"$J$57","v":34.5625},{"$f":"$D$57","v":1.125},{"$f":"$K$57","v":15.6875},{"$f":"$E$57","v":1.5},{"$f":"$L$57","v":12},{"$f":"$F$57","v":2.25},{"$f":"$M$57","v":8.5},{"$f":"$G$57","v":3},{"$f":"$N$57","v":6.9375}]
[null,{"$f":"$B$58","v":6.5},{"$f":"$C$58","v":0.4375},{"$f":"$J$58","v":37.4375},{"$f":"$D$58","v":1.25},{"$f":"$K$58","v":17},{"$f":"$E$58","v":1.625},{"$f":"$L$58","v":13},{"$f":"$F$58","v":2.4375},{"$f":"$M$58","v":9.1875},{"$f":"$G$58","v":3.25},{"$f":"$N$58","v":7.5}]
[null,{"$f":"$B$59","v":7},{"$f":"$C$59","v":0.4375},{"$f":"$J$59","v":40.3125},{"$f":"$D$59","v":1.3125},{"$f":"$K$59","v":18.3125},{"$f":"$E$59","v":1.75},{"$f":"$L$59","v":14},{"$f":"$F$59","v":2.625},{"$f":"$M$59","v":9.875},{"$f":"$G$59","v":3.5},{"$f":"$N$59","v":8.0625}]
[null,{"$f":"$B$60","v":7.5},{"$f":"$C$60","v":0.5},{"$f":"$J$60","v":43.1875},{"$f":"$D$60","v":1.4375},{"$f":"$K$60","v":19.625},{"$f":"$E$60","v":1.875},{"$f":"$L$60","v":15},{"$f":"$F$60","v":2.8125},{"$f":"$M$60","v":10.625},{"$f":"$G$60","v":3.75},{"$f":"$N$60","v":8.6875}]
[null,{"$f":"$B$61","v":8},{"$f":"$C$61","v":0.5},{"$f":"$J$61","v":46.0625},{"$f":"$D$61","v":1.5},{"$f":"$K$61","v":20.875},{"$f":"$E$61","v":2},{"$f":"$L$61","v":16},{"$f":"$F$61","v":3},{"$f":"$M$61","v":11.3125},{"$f":"$G$61","v":4},{"$f":"$N$61","v":9.25}]
[null,{"$f":"$B$62","v":8.5},{"$f":"$C$62","v":0.5625},{"$f":"$J$62","v":48.9375},{"$f":"$D$62","v":1.625},{"$f":"$K$62","v":22.1875},{"$f":"$E$62","v":2.125},{"$f":"$L$62","v":17},{"$f":"$F$62","v":3.1875},{"$f":"$M$62","v":12},{"$f":"$G$62","v":4.25},{"$f":"$N$62","v":9.8125}]
[null,{"$f":"$B$63","v":9},{"$f":"$C$63","v":0.5625},{"$f":"$J$63","v":51.8125},{"$f":"$D$63","v":1.6875},{"$f":"$K$63","v":23.5},{"$f":"$E$63","v":2.25},{"$f":"$L$63","v":18},{"$f":"$F$63","v":3.375},{"$f":"$M$63","v":12.75},{"$f":"$G$63","v":4.5},{"$f":"$N$63","v":10.375}]
[null,{"$f":"$B$64","v":9.5},{"$f":"$C$64","v":0.625},{"$f":"$J$64","v":54.6875},{"$f":"$D$64","v":1.8125},{"$f":"$K$64","v":24.8125},{"$f":"$E$64","v":2.375},{"$f":"$L$64","v":19},{"$f":"$F$64","v":3.5625},{"$f":"$M$64","v":13.4375},{"$f":"$G$64","v":4.75},{"$f":"$N$64","v":11}]
[null,{"$f":"$B$65","v":10},{"$f":"$C$65","v":0.625},{"$f":"$J$65","v":57.5625},{"$f":"$D$65","v":1.875},{"$f":"$K$65","v":26.125},{"$f":"$E$65","v":2.5},{"$f":"$L$65","v":20},{"$f":"$F$65","v":3.75},{"$f":"$M$65","v":14.125},{"$f":"$G$65","v":5},{"$f":"$N$65","v":11.5625}]
[null,{"$f":"$B$66","v":11},{"$f":"$C$66","v":0.6875},{"$f":"$J$66","v":63.375},{"$f":"$D$66","v":2.0625},{"$f":"$K$66","v":28.75},{"$f":"$E$66","v":2.75},{"$f":"$L$66","v":22},{"$f":"$F$66","v":4.125},{"$f":"$M$66","v":15.5625},{"$f":"$G$66","v":5.5},{"$f":"$N$66","v":12.6875}]
[null,{"$f":"$B$67","v":12},{"$f":"$C$67","v":0.75},{"$f":"$J$67","v":69.125},{"$f":"$D$67","v":2.25},{"$f":"$K$67","v":31.375},{"$f":"$E$67","v":3},{"$f":"$L$67","v":24},{"$f":"$F$67","v":4.5},{"$f":"$M$67","v":17},{"$f":"$G$67","v":6},{"$f":"$N$67","v":13.875}]
[null,{"$f":"$B$68","v":13},{"$f":"$C$68","v":0.8125},{"$f":"$J$68","v":74.875},{"$f":"$D$68","v":2.4375},{"$f":"$K$68","v":34},{"$f":"$E$68","v":3.25},{"$f":"$L$68","v":26},{"$f":"$F$68","v":4.875},{"$f":"$M$68","v":18.375},{"$f":"$G$68","v":6.5},{"$f":"$N$68","v":15}]
[null,{"$f":"$B$69","v":14},{"$f":"$C$69","v":0.875},{"$f":"$J$69","v":80.625},{"$f":"$D$69","v":2.625},{"$f":"$K$69","v":36.5625},{"$f":"$E$69","v":3.5},{"$f":"$L$69","v":28},{"$f":"$F$69","v":5.25},{"$f":"$M$69","v":19.8125},{"$f":"$G$69","v":7},{"$f":"$N$69","v":16.1875}]
[null,{"$f":"$B$70","v":15},{"$f":"$C$70","v":0.9375},{"$f":"$J$70","v":86.375},{"$f":"$D$70","v":2.8125},{"$f":"$K$70","v":39.1875},{"$f":"$E$70","v":3.75},{"$f":"$L$70","v":30},{"$f":"$F$70","v":5.625},{"$f":"$M$70","v":21.1875},{"$f":"$G$70","v":7.5},{"$f":"$N$70","v":17.3125}]
[null,{"$f":"$B$71","v":16},{"$f":"$C$71","v":1},{"$f":"$J$71","v":92.125},{"$f":"$D$71","v":3},{"$f":"$K$71","v":41.8125},{"$f":"$E$71","v":4},{"$f":"$L$71","v":32},{"$f":"$F$71","v":6},{"$f":"$M$71","v":22.625},{"$f":"$G$71","v":8},{"$f":"$N$71","v":18.5}]
[null,{"$f":"$B$72","v":17},{"$f":"$C$72","v":1.0625},{"$f":"$J$72","v":97.875},{"$f":"$D$72","v":3.1875},{"$f":"$K$72","v":44.4375},{"$f":"$E$72","v":4.25},{"$f":"$L$72","v":34},{"$f":"$F$72","v":6.375},{"$f":"$M$72","v":24.0625},{"$f":"$G$72","v":8.5},{"$f":"$N$72","v":19.625}]
[null,{"$f":"$B$73","v":18},{"$f":"$C$73","v":1.125},{"$f":"$J$73","v":103.6875},{"$f":"$D$73","v":3.375},{"$f":"$K$73","v":47.0625},{"$f":"$E$73","v":4.5},{"$f":"$L$73","v":36},{"$f":"$F$73","v":6.75},{"$f":"$M$73","v":25.4375},{"$f":"$G$73","v":9},{"$f":"$N$73","v":20.8125}]
[null,{"$f":"$B$74","v":19},{"$f":"$C$74","v":1.1875},{"$f":"$J$74","v":109.4375},{"$f":"$D$74","v":3.5625},{"$f":"$K$74","v":49.625},{"$f":"$E$74","v":4.75},{"$f":"$L$74","v":38},{"$f":"$F$74","v":7.125},{"$f":"$M$74","v":26.875},{"$f":"$G$74","v":9.5},{"$f":"$N$74","v":21.9375}]
[null,{"$f":"$B$75","v":20},{"$f":"$C$75","v":1.25},{"$f":"$J$75","v":115.1875},{"$f":"$D$75","v":3.75},{"$f":"$K$75","v":52.25},{"$f":"$E$75","v":5},{"$f":"$L$75","v":40},{"$f":"$F$75","v":7.5},{"$f":"$M$75","v":28.3125},{"$f":"$G$75","v":10},{"$f":"$N$75","v":23.125}]
[null,{"$f":"$B$76","v":21},{"$f":"$C$76","v":1.3125},{"$f":"$J$76","v":120.9375},{"$f":"$D$76","v":3.9375},{"$f":"$K$76","v":54.875},{"$f":"$E$76","v":5.25},{"$f":"$L$76","v":42},{"$f":"$F$76","v":7.875},{"$f":"$M$76","v":29.6875},{"$f":"$G$76","v":10.5},{"$f":"$N$76","v":24.25}]
[null,{"$f":"$B$77","v":22},{"$f":"$C$77","v":1.375},{"$f":"$J$77","v":126.6875},{"$f":"$D$77","v":4.125},{"$f":"$K$77","v":57.5},{"$f":"$E$77","v":5.5},{"$f":"$L$77","v":44},{"$f":"$F$77","v":8.25},{"$f":"$M$77","v":31.125},{"$f":"$G$77","v":11},{"$f":"$N$77","v":25.375}]
[null,{"$f":"$B$78","v":23},{"$f":"$C$78","v":1.4375},{"$f":"$J$78","v":132.4375},{"$f":"$D$78","v":4.3125},{"$f":"$K$78","v":60.125},{"$f":"$E$78","v":5.75},{"$f":"$L$78","v":46},{"$f":"$F$78","v":8.625},{"$f":"$M$78","v":32.5},{"$f":"$G$78","v":11.5},{"$f":"$N$78","v":26.5625}]
[null,{"$f":"$B$79","v":24},{"$f":"$C$79","v":1.5},{"$f":"$J$79","v":138.1875},{"$f":"$D$79","v":4.5},{"$f":"$K$79","v":62.6875},{"$f":"$E$79","v":6},{"$f":"$L$79","v":48},{"$f":"$F$79","v":9},{"$f":"$M$79","v":33.9375},{"$f":"$G$79","v":12},{"$f":"$N$79","v":27.6875}]
[null,{"$f":"$B$80","v":25},{"$f":"$C$80","v":1.5625},{"$f":"$J$80","v":144},{"$f":"$D$80","v":4.6875},{"$f":"$K$80","v":65.3125},{"$f":"$E$80","v":6.25},{"$f":"$L$80","v":50},{"$f":"$F$80","v":9.375},{"$f":"$M$80","v":35.375},{"$f":"$G$80","v":12.5},{"$f":"$N$80","v":28.875}]

{"sheet":"FormulaFillDown","index":1,"n_rows":44,"n_cols":12,"rows_kept":44,"cut":false,"hidden":false,"merged":[]}
["FROM:","Mark Biegert"]
["SUBJECT:","Conduit Bending Table"]
["DATE:","2018-01-15"]
[]
[]
[null,null,"Angle"]
[null,null,{"$f":"C8","v":10},null,{"$f":"E8","v":22.5},null,{"$f":"G8","v":30},null,{"$f":"I8","v":45},null,{"$f":"K8","v":60}]
[null,null,10,10,22.5,22.5,30,30,45,45,60,60]
[null,"Bend Offset","Shrinkage","Bend Dist.","Shrinkage","Bend Dist.","Shrinkage","Bend Dist.","Shrinkage","Bend Dist.","Shrinkage","Bend Dist."]
[null,0.5,{"$f":"MROUND(MROUND((_xlfn.CSC(C$8*PI()/180)-_xlfn.COT(C$8*PI()/180)),1/16)*$B10,1/16)","v":6.25E-2},{"$f":"MROUND(ROUND(_xlfn.CSC(D$8*PI()/180),4)*$B10,1/16)","v":2.875},{"$f":"MROUND(MROUND((_xlfn.CSC(E$8*PI()/180)-_xlfn.COT(E$8*PI()/180)),1/16)*$B10,1/16)","v":0.125},{"$f":"MROUND(ROUND(_xlfn.CSC(F$8*PI()/180),4)*$B10,1/16)","v":1.3125},{"$f":"MROUND(MROUND((_xlfn.CSC(G$8*PI()/180)-_xlfn.COT(G$8*PI()/180)),1/16)*$B10,1/16)","v":0.125},{"$f":"MROUND(ROUND(_xlfn.CSC(H$8*PI()/180),4)*$B10,1/16)","v":1},{"$f":"MROUND(MROUND((_xlfn.CSC(I$8*PI()/180)-_xlfn.COT(I$8*PI()/180)),1/16)*$B10,1/16)","v":0.25},{"$f":"MROUND(ROUND(_xlfn.CSC(J$8*PI()/180),4)*$B10,1/16)","v":0.6875},{"$f":"MROUND(MROUND((_xlfn.CSC(K$8*PI()/180)-_xlfn.COT(K$8*PI()/180)),1/16)*$B10,1/16)","v":0.3125},{"$f":"MROUND(ROUND(_xlfn.CSC(L$8*PI()/180),4)*$B10,1/16)","v":0.5625}]
[null,1,{"$f":"MROUND(MROUND((_xlfn.CSC(C$8*PI()/180)-_xlfn.COT(C$8*PI()/180)),1/16)*$B11,1/16)","v":6.25E-2},{"$f":"MROUND(ROUND(_xlfn.CSC(D$8*PI()/180),4)*$B11,1/16)","v":5.75},0.1875,2.625,0.25,2,0.4375,1.4375,0.5625,1.125]
[null,1.5,0.125,8.625,0.3125,3.9375,0.375,3,0.6875,2.125,0.875,1.75]
[null,2,0.125,11.5,0.375,5.25,0.5,4,0.875,2.8125,1.125,2.3125]
[null,2.5,0.1875,14.375,0.5,6.5625,0.625,5,1.125,3.5625,1.4375,2.875]
[null,3,0.1875,17.25,0.5625,7.8125,0.75,6,1.3125,4.25,1.6875,3.4375]
[null,3.5,0.25,20.125,0.6875,9.125,0.875,7,1.5625,4.9375,2,4.0625]
[null,4,0.25,23.0625,0.75,10.4375,1,8,1.75,5.6875,2.25,4.625]
[null,4.5,0.3125,25.9375,0.875,11.75,1.125,9,2,6.375,2.5625,5.1875]
[null,5,0.3125,28.8125,0.9375,13.0625,1.25,10,2.1875,7.0625,2.8125,5.75]
[null,5.5,0.375,31.6875,1.0625,14.375,1.375,11,2.4375,7.75,3.125,6.375]
[null,6,0.375,34.5625,1.125,15.6875,1.5,12,2.625,8.5,3.375,6.9375]
[null,6.5,0.4375,37.4375,1.25,17,1.625,13,2.875,9.1875,3.6875,7.5]
[null,7,0.4375,40.3125,1.3125,18.3125,1.75,14,3.0625,9.875,3.9375,8.0625]
[null,7.5,0.5,43.1875,1.4375,19.625,1.875,15,3.3125,10.625,4.25,8.6875]
[null,8,0.5,46.0625,1.5,20.875,2,16,3.5,11.3125,4.5,9.25]
[null,8.5,0.5625,48.9375,1.625,22.1875,2.125,17,3.75,12,4.8125,9.8125]
[null,9,0.5625,51.8125,1.6875,23.5,2.25,18,3.9375,12.75,5.0625,10.375]
[null,9.5,0.625,54.6875,1.8125,24.8125,2.375,19,4.1875,13.4375,5.375,11]
[null,10,0.625,57.5625,1.875,26.125,2.5,20,4.375,14.125,5.625,11.5625]
[null,11,0.6875,63.375,2.0625,28.75,2.75,22,4.8125,15.5625,6.1875,12.6875]
[null,12,0.75,69.125,2.25,31.375,3,24,5.25,17,6.75,13.875]
[null,13,0.8125,74.875,2.4375,34,3.25,26,5.6875,18.375,7.3125,15]
[null,14,0.875,80.625,2.625,36.5625,3.5,28,6.125,19.8125,7.875,16.1875]
[null,15,0.9375,86.375,2.8125,39.1875,3.75,30,6.5625,21.1875,8.4375,17.3125]
[null,16,1,92.125,3,41.8125,4,32,7,22.625,9,18.5]
[null,17,1.0625,97.875,3.1875,44.4375,4.25,34,7.4375,24.0625,9.5625,19.625]
[null,18,1.125,103.6875,3.375,47.0625,4.5,36,7.875,25.4375,10.125,20.8125]
[null,19,1.1875,109.4375,3.5625,49.625,4.75,38,8.3125,26.875,10.6875,21.9375]
[null,20,1.25,115.1875,3.75,52.25,5,40,8.75,28.3125,11.25,23.125]
[null,21,1.3125,120.9375,3.9375,54.875,5.25,42,9.1875,29.6875,11.8125,24.25]
[null,22,1.375,126.6875,4.125,57.5,5.5,44,9.625,31.125,12.375,25.375]
[null,23,1.4375,132.4375,4.3125,60.125,5.75,46,10.0625,32.5,12.9375,26.5625]
[null,24,1.5,138.1875,4.5,62.6875,6,48,10.5,33.9375,13.5,27.6875]
[null,25,1.5625,144,4.6875,65.3125,6.25,50,10.9375,35.375,14.0625,28.875]

{"sheet":"BendRadiusVersion","index":2,"n_rows":57,"n_cols":17,"rows_kept":57,"cut":false,"hidden":false,"merged":[]}
["FROM:","Mark Biegert"]
["SUBJECT:","Detailed Model "]
["DATE:","2018-01-18",null,null,"NA means that this angle offset combination is not possible."]
[null,null,null,null,"A shallower angle should be used. The combination is not possible"]
[null,"Bend Radius",4,"in","because the bend radius is so large so as to preclude a straight section."]
[]
[null,null,"Angle"]
[null,null,10,null,null,22.5,null,null,30,null,null,45,null,null,60]
[null,null,{"$f":"C8","v":10},{"$f":"C8","v":10},{"$f":"C8","v":10},{"$f":"F8","v":22.5},{"$f":"F8","v":22.5},{"$f":"F8","v":22.5},{"$f":"I8","v":30},{"$f":"I8","v":30},{"$f":"I8","v":30},{"$f":"L8","v":45},{"$f":"L8","v":45},{"$f":"L8","v":45},{"$f":"O8","v":60},{"$f":"O8","v":60},{"$f":"O8","v":60}]
[null,"Bend Offset","Shrinkage","Straight Length","C-to-C Bend Dist","Shrinkage","Straight Length","C-to-C Bend Dist","Shrinkage","Straight Length","C-to-C Bend Dist","Shrinkage","Straight Length","C-to-C Bend Dist","Shrinkage","Straight Length","C-to-C Bend Dist"]
[null,0.5,{"$f":"MROUND(($B11-4*_R)*TAN(C$9*PI()/360)+2*_R*C$9*PI()/180,1/16)","v":6.25E-2},{"$f":"MROUND(($B11-2*_R*(1-COS(D$9*PI()/180)))*_xlfn.CSC(D$9*PI()/180),1/16)","v":2.1875},{"$f":"MROUND(($B11-2*_R*(1-COS(E$9*PI()/180)))*_xlfn.CSC(E$9*PI()/180)+_R*E$9*PI()/180,1/16)","v":2.875},{"$f":"MROUND(($B11-4*_R)*TAN(F$9*PI()/360)+2*_R*F$9*PI()/180,1/16*SIGN(($B11-4*_R)*TAN(F$9*PI()/360)+2*_R*F$9*PI()/180))","v":6.25E-2},{"$f":"MROUND(($B11-2*_R*(1-COS(G$9*PI()/180)))*_xlfn.CSC(G$9*PI()/180),1/16*SIGN(($B11-2*_R*(1-COS(G$9*PI()/180)))*_xlfn.CSC(G$9*PI()/180)))","v":-0.3125},{"$f":"MROUND(($B11-2*_R*(1-COS(H$9*PI()/180)))*_xlfn.CSC(H$9*PI()/180)+_R*H$9*PI()/180,1/16*SIGN(($B11-2*_R*(1-COS(H$9*PI()/180)))*_xlfn.CSC(H$9*PI()/180)+_R*H$9*PI()/180))","v":1.3125},{"$f":"MROUND(($B11-4*_R)*TAN(I$9*PI()/360)+2*_R*I$9*PI()/180,1/16*SIGN(($B11-4*_R)*TAN(I$9*PI()/360)+2*_R*I$9*PI()/180))","v":6.25E-2},{"$f":"MROUND(($B11-2*_R*(1-COS(J$9*PI()/180)))*_xlfn.CSC(J$9*PI()/180),1/16*SIGN(($B11-2*_R*(1-COS(J$9*PI()/180)))*_xlfn.CSC(J$9*PI()/180)))","v":-1.125},{"$f":"MROUND(($B11-2*_R*(1-COS(K$9*PI()/180)))*_xlfn.CSC(K$9*PI()/180)+_R*K$9*PI()/180,1/16*SIGN(($B11-2*_R*(1-COS(K$9*PI()/180)))*_xlfn.CSC(K$9*PI()/180)+_R*K$9*PI()/180))","v":0.9375},{"$f":"MROUND(($B11-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B11-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":-0.125},{"$f":"MROUND(($B11-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B11-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":-2.625},{"$f":"MROUND(($B11-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B11-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":0.5625},{"$f":"MROUND(($B11-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B11-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":-0.5625},{"$f":"MROUND(($B11-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B11-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":-4.0625},{"$f":"MROUND(($B11-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B11-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":0.125}]
[null,1,6.25E-2,5.0625,5.75,0.1875,1,2.5625,0.1875,-0.125,1.9375,{"$f":"MROUND(($B12-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B12-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":6.25E-2},{"$f":"MROUND(($B12-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B12-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":-1.875},{"$f":"MROUND(($B12-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B12-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":1.25},{"$f":"MROUND(($B12-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B12-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":-0.3125},{"$f":"MROUND(($B12-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B12-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":-3.4375},{"$f":"MROUND(($B12-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B12-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":0.75}]
[null,1.5,0.125,7.9375,8.625,0.25,2.3125,3.875,0.3125,0.875,2.9375,{"$f":"MROUND(($B13-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B13-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":0.25},{"$f":"MROUND(($B13-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B13-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":-1.1875},{"$f":"MROUND(($B13-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B13-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":1.9375},{"$f":"MROUND(($B13-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B13-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":0},{"$f":"MROUND(($B13-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B13-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":-2.875},{"$f":"MROUND(($B13-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B13-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":1.3125}]
[null,2,0.1875,10.8125,11.5,0.375,3.625,5.1875,0.4375,1.875,3.9375,{"$f":"MROUND(($B14-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B14-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":0.5},{"$f":"MROUND(($B14-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B14-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":-0.5},{"$f":"MROUND(($B14-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B14-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":2.6875},{"$f":"MROUND(($B14-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B14-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":0.3125},{"$f":"MROUND(($B14-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B14-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":-2.3125},{"$f":"MROUND(($B14-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B14-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":1.875}]
[null,2.5,0.1875,13.6875,14.375,0.4375,4.9375,6.5,0.5625,2.875,4.9375,{"$f":"MROUND(($B15-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B15-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":0.6875},{"$f":"MROUND(($B15-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B15-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":0.25},{"$f":"MROUND(($B15-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B15-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":3.375},{"$f":"MROUND(($B15-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B15-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":0.5625},{"$f":"MROUND(($B15-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B15-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":-1.75},{"$f":"MROUND(($B15-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B15-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":2.4375}]
[null,3,0.25,16.5625,17.25,0.5625,6.25,7.8125,0.6875,3.875,5.9375,{"$f":"MROUND(($B16-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B16-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":0.875},{"$f":"MROUND(($B16-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B16-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":0.9375},{"$f":"MROUND(($B16-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B16-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":4.0625},{"$f":"MROUND(($B16-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B16-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":0.875},{"$f":"MROUND(($B16-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B16-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":-1.125},{"$f":"MROUND(($B16-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B16-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":3.0625}]
[null,3.5,0.3125,19.4375,20.125,0.625,7.5625,9.125,0.8125,4.875,6.9375,{"$f":"MROUND(($B17-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B17-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":1.125},{"$f":"MROUND(($B17-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B17-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":1.625},{"$f":"MROUND(($B17-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B17-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":4.75},{"$f":"MROUND(($B17-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B17-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":1.1875},{"$f":"MROUND(($B17-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B17-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":-0.5625},{"$f":"MROUND(($B17-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B17-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":3.625}]
[null,4,0.375,22.3125,23.0625,0.75,8.875,10.4375,1,5.875,7.9375,{"$f":"MROUND(($B18-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B18-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":1.3125},{"$f":"MROUND(($B18-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B18-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":2.3125},{"$f":"MROUND(($B18-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B18-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":5.5},{"$f":"MROUND(($B18-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B18-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":1.4375},{"$f":"MROUND(($B18-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B18-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":0},{"$f":"MROUND(($B18-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B18-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":4.1875}]
[null,4.5,0.375,25.1875,25.9375,0.875,10.1875,11.75,1.125,6.875,8.9375,{"$f":"MROUND(($B19-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B19-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":1.5},{"$f":"MROUND(($B19-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B19-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":3.0625},{"$f":"MROUND(($B19-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B19-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":6.1875},{"$f":"MROUND(($B19-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B19-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":1.75},{"$f":"MROUND(($B19-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B19-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":0.5625},{"$f":"MROUND(($B19-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B19-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":4.75}]
[null,5,0.4375,28.125,28.8125,0.9375,11.5,13.0625,1.25,7.875,9.9375,{"$f":"MROUND(($B20-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B20-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":1.75},{"$f":"MROUND(($B20-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B20-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":3.75},{"$f":"MROUND(($B20-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B20-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":6.875},{"$f":"MROUND(($B20-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B20-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":2},{"$f":"MROUND(($B20-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B20-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":1.125},{"$f":"MROUND(($B20-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B20-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":5.3125}]
[null,5.5,0.5,31,31.6875,1.0625,12.75,14.375,1.375,8.875,10.9375,{"$f":"MROUND(($B21-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B21-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":1.9375},{"$f":"MROUND(($B21-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B21-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":4.4375},{"$f":"MROUND(($B21-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B21-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":7.625},{"$f":"MROUND(($B21-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B21-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":2.3125},{"$f":"MROUND(($B21-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B21-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":1.75},{"$f":"MROUND(($B21-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B21-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":5.9375}]
[null,6,0.5,33.875,34.5625,1.125,14.0625,15.6875,1.5,9.875,11.9375,{"$f":"MROUND(($B22-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B22-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":2.125},{"$f":"MROUND(($B22-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B22-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":5.1875},{"$f":"MROUND(($B22-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B22-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":8.3125},{"$f":"MROUND(($B22-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B22-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":2.625},{"$f":"MROUND(($B22-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B22-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":2.3125},{"$f":"MROUND(($B22-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B22-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":6.5}]
[null,6.5,0.5625,36.75,37.4375,1.25,15.375,16.9375,1.625,10.875,12.9375,{"$f":"MROUND(($B23-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B23-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":2.375},{"$f":"MROUND(($B23-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B23-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":5.875},{"$f":"MROUND(($B23-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B23-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":9},{"$f":"MROUND(($B23-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B23-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":2.875},{"$f":"MROUND(($B23-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B23-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":2.875},{"$f":"MROUND(($B23-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B23-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":7.0625}]
[null,7,0.625,39.625,40.3125,1.375,16.6875,18.25,1.75,11.875,13.9375,{"$f":"MROUND(($B24-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B24-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":2.5625},{"$f":"MROUND(($B24-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B24-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":6.5625},{"$f":"MROUND(($B24-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B24-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":9.75},{"$f":"MROUND(($B24-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B24-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":3.1875},{"$f":"MROUND(($B24-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B24-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":3.4375},{"$f":"MROUND(($B24-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B24-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":7.625}]
[null,7.5,0.625,42.5,43.1875,1.4375,18,19.5625,1.9375,12.875,14.9375,{"$f":"MROUND(($B25-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B25-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":2.75},{"$f":"MROUND(($B25-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B25-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":7.3125},{"$f":"MROUND(($B25-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B25-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":10.4375},{"$f":"MROUND(($B25-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B25-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":3.5},{"$f":"MROUND(($B25-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B25-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":4.0625},{"$f":"MROUND(($B25-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B25-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":8.25}]
[null,8,0.6875,45.375,46.0625,1.5625,19.3125,20.875,2.0625,13.875,15.9375,{"$f":"MROUND(($B26-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B26-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":3},{"$f":"MROUND(($B26-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B26-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":8},{"$f":"MROUND(($B26-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B26-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":11.125},{"$f":"MROUND(($B26-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B26-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":3.75},{"$f":"MROUND(($B26-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B26-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":4.625},{"$f":"MROUND(($B26-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B26-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":8.8125}]
[null,8.5,0.75,48.25,48.9375,1.625,20.625,22.1875,2.1875,14.875,16.9375,{"$f":"MROUND(($B27-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B27-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":3.1875},{"$f":"MROUND(($B27-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B27-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":8.6875},{"$f":"MROUND(($B27-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B27-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":11.875},{"$f":"MROUND(($B27-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B27-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":4.0625},{"$f":"MROUND(($B27-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B27-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":5.1875},{"$f":"MROUND(($B27-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B27-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":9.375}]
[null,9,0.8125,51.125,51.8125,1.75,21.9375,23.5,2.3125,15.875,17.9375,{"$f":"MROUND(($B28-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B28-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":3.375},{"$f":"MROUND(($B28-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B28-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":9.4375},{"$f":"MROUND(($B28-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B28-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":12.5625},{"$f":"MROUND(($B28-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B28-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":4.3125},{"$f":"MROUND(($B28-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B28-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":5.75},{"$f":"MROUND(($B28-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B28-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":9.9375}]
[null,9.5,0.8125,54,54.6875,1.875,23.25,24.8125,2.4375,16.875,18.9375,{"$f":"MROUND(($B29-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B29-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":3.5625},{"$f":"MROUND(($B29-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B29-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":10.125},{"$f":"MROUND(($B29-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B29-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":13.25},{"$f":"MROUND(($B29-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B29-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":4.625},{"$f":"MROUND(($B29-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B29-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":6.375},{"$f":"MROUND(($B29-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B29-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":10.5625}]
[null,10,0.875,56.875,57.5625,1.9375,24.5625,26.125,2.5625,17.875,19.9375,{"$f":"MROUND(($B30-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B30-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":3.8125},{"$f":"MROUND(($B30-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B30-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":10.8125},{"$f":"MROUND(($B30-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B30-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":14},{"$f":"MROUND(($B30-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B30-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":4.9375},{"$f":"MROUND(($B30-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B30-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":6.9375},{"$f":"MROUND(($B30-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B30-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":11.125}]
[null,11,0.9375,62.625,63.375,2.125,27.125,28.75,2.875,19.875,21.9375,{"$f":"MROUND(($B31-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B31-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":4.1875},{"$f":"MROUND(($B31-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B31-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":12.25},{"$f":"MROUND(($B31-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B31-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":15.375},{"$f":"MROUND(($B31-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B31-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":5.5},{"$f":"MROUND(($B31-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B31-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":8.0625},{"$f":"MROUND(($B31-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B31-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":12.25}]
[null,12,1.0625,68.375,69.125,2.375,29.75,31.3125,3.125,21.875,23.9375,{"$f":"MROUND(($B32-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B32-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":4.625},{"$f":"MROUND(($B32-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B32-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":13.6875},{"$f":"MROUND(($B32-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B32-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":16.8125},{"$f":"MROUND(($B32-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B32-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":6.0625},{"$f":"MROUND(($B32-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B32-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":9.25},{"$f":"MROUND(($B32-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B32-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":13.4375}]
[null,13,1.125,74.1875,74.875,2.5625,32.375,33.9375,3.375,23.875,25.9375,{"$f":"MROUND(($B33-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B33-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":5.0625},{"$f":"MROUND(($B33-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B33-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":15.0625},{"$f":"MROUND(($B33-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B33-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":18.1875},{"$f":"MROUND(($B33-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B33-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":6.625},{"$f":"MROUND(($B33-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B33-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":10.375},{"$f":"MROUND(($B33-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B33-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":14.5625}]
[null,14,1.25,79.9375,80.625,2.75,35,36.5625,3.625,25.875,27.9375,{"$f":"MROUND(($B34-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B34-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":5.4375},{"$f":"MROUND(($B34-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B34-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":16.5},{"$f":"MROUND(($B34-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B34-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":19.625},{"$f":"MROUND(($B34-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B34-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":7.25},{"$f":"MROUND(($B34-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B34-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":11.5625},{"$f":"MROUND(($B34-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B34-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":15.75}]
[null,15,1.3125,85.6875,86.375,2.9375,37.625,39.1875,3.9375,27.875,29.9375,{"$f":"MROUND(($B35-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B35-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":5.875},{"$f":"MROUND(($B35-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B35-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":17.875},{"$f":"MROUND(($B35-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B35-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":21.0625},{"$f":"MROUND(($B35-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B35-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":7.8125},{"$f":"MROUND(($B35-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B35-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":12.6875},{"$f":"MROUND(($B35-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B35-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":16.875}]
[null,16,1.375,91.4375,92.125,3.125,40.1875,41.8125,4.1875,29.875,31.9375,{"$f":"MROUND(($B36-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B36-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":6.3125},{"$f":"MROUND(($B36-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B36-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":19.3125},{"$f":"MROUND(($B36-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B36-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":22.4375},{"$f":"MROUND(($B36-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B36-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":8.375},{"$f":"MROUND(($B36-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B36-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":13.875},{"$f":"MROUND(($B36-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B36-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":18.0625}]
[null,17,1.5,97.1875,97.875,3.3125,42.8125,44.375,4.4375,31.875,33.9375,{"$f":"MROUND(($B37-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B37-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":6.6875},{"$f":"MROUND(($B37-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B37-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":20.75},{"$f":"MROUND(($B37-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B37-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":23.875},{"$f":"MROUND(($B37-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B37-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":8.9375},{"$f":"MROUND(($B37-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B37-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":15},{"$f":"MROUND(($B37-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B37-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":19.1875}]
[null,18,1.5625,102.9375,103.625,3.5625,45.4375,47,4.75,33.875,35.9375,{"$f":"MROUND(($B38-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B38-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":7.125},{"$f":"MROUND(($B38-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B38-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":22.125},{"$f":"MROUND(($B38-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B38-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":25.3125},{"$f":"MROUND(($B38-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B38-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":9.5625},{"$f":"MROUND(($B38-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B38-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":16.1875},{"$f":"MROUND(($B38-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B38-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":20.375}]
[null,19,1.6875,108.6875,109.4375,3.75,48.0625,49.625,5,35.875,37.9375,{"$f":"MROUND(($B39-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B39-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":7.5},{"$f":"MROUND(($B39-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B39-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":23.5625},{"$f":"MROUND(($B39-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B39-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":26.6875},{"$f":"MROUND(($B39-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B39-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":10.125},{"$f":"MROUND(($B39-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B39-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":17.3125},{"$f":"MROUND(($B39-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B39-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":21.5}]
[null,20,1.75,114.5,115.1875,3.9375,50.6875,52.25,5.25,37.875,39.9375,{"$f":"MROUND(($B40-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B40-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":7.9375},{"$f":"MROUND(($B40-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B40-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":25},{"$f":"MROUND(($B40-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B40-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":28.125},{"$f":"MROUND(($B40-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B40-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":10.6875},{"$f":"MROUND(($B40-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B40-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":18.5},{"$f":"MROUND(($B40-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B40-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":22.6875}]
[null,21,1.8125,120.25,120.9375,4.125,53.3125,54.875,5.5,39.875,41.9375,{"$f":"MROUND(($B41-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B41-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":8.375},{"$f":"MROUND(($B41-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B41-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":26.375},{"$f":"MROUND(($B41-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B41-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":29.5},{"$f":"MROUND(($B41-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B41-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":11.25},{"$f":"MROUND(($B41-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B41-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":19.625},{"$f":"MROUND(($B41-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B41-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":23.8125}]
[null,22,1.9375,126,126.6875,4.3125,55.875,57.4375,5.8125,41.875,43.9375,{"$f":"MROUND(($B42-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B42-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":8.75},{"$f":"MROUND(($B42-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B42-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":27.8125},{"$f":"MROUND(($B42-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B42-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":30.9375},{"$f":"MROUND(($B42-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B42-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":11.8125},{"$f":"MROUND(($B42-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B42-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":20.8125},{"$f":"MROUND(($B42-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B42-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":25}]
[null,23,2,131.75,132.4375,4.5625,58.5,60.0625,6.0625,43.875,45.9375,{"$f":"MROUND(($B43-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B43-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":9.1875},{"$f":"MROUND(($B43-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B43-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":29.1875},{"$f":"MROUND(($B43-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B43-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":32.375},{"$f":"MROUND(($B43-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B43-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":12.4375},{"$f":"MROUND(($B43-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B43-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":21.9375},{"$f":"MROUND(($B43-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B43-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":26.125}]
[null,24,2.125,137.5,138.1875,4.75,61.125,62.6875,6.3125,45.875,47.9375,{"$f":"MROUND(($B44-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B44-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":9.625},{"$f":"MROUND(($B44-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B44-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":30.625},{"$f":"MROUND(($B44-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B44-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":33.75},{"$f":"MROUND(($B44-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B44-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":13},{"$f":"MROUND(($B44-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B44-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":23.125},{"$f":"MROUND(($B44-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B44-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":27.3125}]
[null,25,2.1875,143.25,143.9375,4.9375,63.75,65.3125,6.625,47.875,49.9375,{"$f":"MROUND(($B45-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180,1/16*SIGN(($B45-4*_R)*TAN(L$9*PI()/360)+2*_R*L$9*PI()/180))","v":10},{"$f":"MROUND(($B45-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180),1/16*SIGN(($B45-2*_R*(1-COS(M$9*PI()/180)))*_xlfn.CSC(M$9*PI()/180)))","v":32.0625},{"$f":"MROUND(($B45-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180,1/16*SIGN(($B45-2*_R*(1-COS(N$9*PI()/180)))*_xlfn.CSC(N$9*PI()/180)+_R*N$9*PI()/180))","v":35.1875},{"$f":"MROUND(($B45-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180,1/16*SIGN(($B45-4*_R)*TAN(O$9*PI()/360)+2*_R*O$9*PI()/180))","v":13.5625},{"$f":"MROUND(($B45-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180),1/16*SIGN(($B45-2*_R*(1-COS(P$9*PI()/180)))*_xlfn.CSC(P$9*PI()/180)))","v":24.25},{"$f":"MROUND(($B45-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180,1/16*SIGN(($B45-2*_R*(1-COS(Q$9*PI()/180)))*_xlfn.CSC(Q$9*PI()/180)+_R*Q$9*PI()/180))","v":28.4375}]
[]
[]
["Development of Standard Reference Table"]
[]
[null,"Bend Offset",8,"in","Grab the table value from above and divide"]
[null,null,null,null,"by the bend offset to normalize."]
[null,"Angle","Shrinkage","Bend Mult."]
[null,10,{"$f":"MROUND(INDEX($C$11:$Q$45,MATCH(_BO,$B$11:$B$45,0),1+3*(ROWS($C$53:C53)-1))/_BO,1/16)","v":6.25E-2},{"$f":"INDEX($C$11:$Q$45,MATCH(_BO,$B$11:$B$45,0),3+3*(ROWS($C$53:C53)-1))/_BO","v":5.7578125}]
[null,22.5,{"$f":"MROUND(INDEX($C$11:$Q$45,MATCH(_BO,$B$11:$B$45,0),1+3*(ROWS($C$53:C54)-1))/_BO,1/16)","v":0.1875},{"$f":"INDEX($C$11:$Q$45,MATCH(_BO,$B$11:$B$45,0),3+3*(ROWS($C$53:C54)-1))/_BO","v":2.609375}]
[null,30,{"$f":"MROUND(INDEX($C$11:$Q$45,MATCH(_BO,$B$11:$B$45,0),1+3*(ROWS($C$53:C55)-1))/_BO,1/16)","v":0.25},{"$f":"INDEX($C$11:$Q$45,MATCH(_BO,$B$11:$B$45,0),3+3*(ROWS($C$53:C55)-1))/_BO","v":1.9921875}]
[null,45,{"$f":"MROUND(INDEX($C$11:$Q$45,MATCH(_BO,$B$11:$B$45,0),1+3*(ROWS($C$53:C56)-1))/_BO,1/16)","v":0.375},{"$f":"INDEX($C$11:$Q$45,MATCH(_BO,$B$11:$B$45,0),3+3*(ROWS($C$53:C56)-1))/_BO","v":1.390625}]
[null,60,{"$f":"MROUND(INDEX($C$11:$Q$45,MATCH(_BO,$B$11:$B$45,0),1+3*(ROWS($C$53:C57)-1))/_BO,1/16)","v":0.5},{"$f":"INDEX($C$11:$Q$45,MATCH(_BO,$B$11:$B$45,0),3+3*(ROWS($C$53:C57)-1))/_BO","v":1.1015625}]